## Slide 1
TSPR
The Total System Performance Ratio
Duane Jonlin, FAIA
Energy Code Advisor
City of Seattle
Supriya Goel
Research Engineer PNNL
Michael Rosenberg
Chief Scientist PNNL

## Slide 2: These are both big dogs
Current codes: Any HVAC system can be a “big dog”
  Because it’s compared only to others of the same “breed”
No penalty for using lousy HVAC system type
No reward for using great system type
No pressure on industry to improve performance
  Or to think holistically

## Slide 3: Whole-Building Compliance Paths Already in Code
Envelope
Lighting
HVAC

## Slide 4: Heating + Cooling Output
Carbon Emissions
TSPR =
(annual)
….for the whole building
(more like a seasonal heat pump rating than a boiler rating)

## Slide 5: But, why not use a “Mechanical Power Allowance,” like lighting power?
Lighting is mostly “on” when spaces are occupied
  Installed capacity is meaningful
HVAC always runs at part load
  …and internal loads vary
  …and envelope loads vary
Annual carbon pollution is what counts, not peak system capacity

## Slide 6: So, what’s that ratio thing again?
  Annual HVAC Loads =
  Annual HVAC Carbon =
Proposed TSPR ≥ Baseline TSPR
Design meets all other HVAC code requirements
  Sum of HVAC coil loads
  - Ideal Loads in EnergyPlus
  - Sum Zone Loads in DOE2
  Sum of annual carbon emissions - for heating, cooling, fans, pumps, energy recovery & heat rejection

## Slide 7: It’s like ASHRAE Appendix G
(Although carbon emissions is metric, not energy cost)
Baseline is a “good” system for each building type
It’s not like IECC C407
One stable baseline
  Not dif for each system type
  Not dif for each code edition
Trades within HVAC only
  Not trading better HVAC for worse envelope
Free calculation tool
  Uses simplified building geometry & defaults

## Slide 8: The Missing Link
Outcome-Based Code
Prove it with performance
Performance Code
One target for whole building
Whole-Building (HVAC) TSPR
Entire system evaluation, like lighting and envelope
Prescriptive Code
Each element complies independently
Also,
A step closer to performance & outcome-based codes

## Slide 9: Code language is pretty simple
C403.1.1 Total System Performance Ratio. For systems serving office, retail, library, and education occupancies subject to the requirements of Section C403.3.5, the Total System Performance Ratio (TSPR) of the proposed design HVAC system shall be greater than or equal to the TSPR of the standard reference design as calculated according to Normative Appendix A, Calculation of Total System Performance Ratio.
Exceptions:
  1. HVAC systems using district heating water, chilled water, or steam.
  2. Chilled beam systems, hybrid central plants, heat-recovery chillers
  3. Systems with chilled water supplied by absorption chillers
  4. Heating only systems,
  5. Buildings complying with Section C407, Total Building Performance Path
  6. Alterations to existing buildings that do not substantially replace the entire HVAC system.
(Ruleset lives in the appendix)

## Slide 10: Help from all over

## Slide 11: Baseline HVAC Systems
Continually running packaged heat pump  cycling heat pump with DOAS/ERV
Small Office/Library
VAV reheat w/boiler and WC chiller  WLHP w/DOAS/ERV
Continually running packaged gas/dx  cycling heat pump with DOAS/ERV
Packaged VAV reheat w/boiler  cycling heat pump with DOAS/ERV
Large Office
School
Stand-alone Retail

## Slide 12: If you insist on all that detail…
Parameter | Building Type |  |  | 
 | Large Office1 | Small Office1 | Retail | School
System Type | Water-source Heat Pump | Packaged air-source Heat Pump | Packaged air-source Heat Pump | Packaged air-source Heat Pump
Fan control | Cycle on load | Cycle on load | Cycle on load | Cycle on load
Space condition fan power (W/cfm) | 0.528 | 0.528 | 0.522 | 0.528
 | (2.5”, 65% fan, 85.5% motor) | (2.5”, 65% fan, 85.5% motor) | (2.5”, 65% fan, 86.5% motor) | (2.5”, 65% fan, 85.5% motor)
Cooling Source | DX (heat pump) | DX (heat pump) | DX (heat pump) | DX (heat pump)
Heat source | Heat Pump | Heat Pump | Heat Pump | Heat Pump
Supplemental heating availability | NA | <40°F | <40°F | <40°F
Modeled cooling/heating COP (Net of fan) | 4.46/4.61 | 3.83/3.81 | 4.25/3.57 | 3.83/3.81
 | 17-65 MBh: 13 EER/4.3 COP | <65 MBh: 14 SEER/8.0 HSPF | 65-135 MBh: 12.2 EER/3.3 COP | <65 MBh: 14 SEER/8.0HSPF 14.0
OSA Economizer | No | No | Yes | Yes
Occupied ventilation source | DOAS | DOAS | DOAS | DOAS
DOAS Fan Power (W/cfm) | 0.979 | 0.979 | 0.873 | 0.887
 | (2.29”, 65% fan, 81% motor) | (2.29”, 65% fan, 81% motor) | (2.29”, 65% fan, 81% motor) | (2.29”, 65% fan, 81% motor)
DOAS temperature control | Bypass | Wild | Bypass | Bypass
ERV efficiency (sensible only) | 70% | 70% | 70% | 70%

## Slide 13: Compliance calculation tool
  New module on top of DOE’s (free) Asset Score Tool
  Simplified tool for assessing building energy efficiency
  Generates a basic energy efficiency rating
  Typical C407 Energy Model Asset Score Simplified Model
  Uses default ASHRAE Appendix C loads and schedules
  Lighting and envelope loads same as baseline

## Slide 14: Asset Score TSPR Tool Workflow

## Slide 15: Landing Page & Report Format

## Slide 16: TSPR Large Office Example

## Slide 17: The TSPR drives down real HVAC energy use and carbon emissions (without changing minimum equipment efficiencies)
Rewards your integrated & efficient system design
Provides free calculation tool for simple, streamlined scoring
Easily tailored for your jurisdiction:
  Pick your preferred baseline systems
  Pick your metric: carbon, cost, site energy, source energy
  Pick your target score
  Apply to beyond code programs
This is not a drill.

## Slide 18: The TSPR drives down real HVAC energy use and carbon emissions (without changing minimum equipment efficiencies)
Rewards your integrated & efficient system design
Provides free calculation tool for simple, streamlined scoring
Easily tailored for your state or city:
  Pick your preferred baseline systems
  Pick your metric: carbon, cost, site energy, source energy
  Pick your target score
Friday’s Late-Breaking News!
Washington State’s Energy Code Technical Advisory Group just voted in favor of the TSPR.
Next up: State Building Code Council debate

## Slide 19: Thank you!
Duane Jonlin
City of Seattle
duane.jonlin@seattle.gov
Michael Rosenberg
Pacific Northwest National Laboratory
Michael.Rosenberg@pnnl.gov
Supriya Goel
Pacific Northwest National Laboratory
Supriya.Goel@pnnl.gov

## Slide 20: Backup Slides

## Slide 21: Large Office Test Case Details
System Type | Baseline: DOAS + WLHP | DOAS + FCU |  | VAV with HW Reheat |  | VAV with Electric Reheat | 
TSPR Results | 14.916 | 13.2085 | 15.4039 | 12.6341 | 16.7315 | 11.3472 | 16.4178
Primary Heating and Cooling System |  |  |  |  |  |  | 
Heating Source, Efficiency | Heat Pump, 4.61 COP | Boiler, 80% | Boiler, 96% | Boiler, 80% Et | Boiler, 92%, Et | Electric Resiatance Furnace, 100% Et | Electric Resiatance Furnace, 100% Et
Boiler Pump Power | NA | 16 W/GPM | 12.8 W/GPM |  |  |  | 
Cooling Source, Efficiency | DX, 4.46 COP | Air Cooled Chiller, 2.843 COP | Air Cooled Chiller, 3.077 COP | Water Cooled Chiller, 4.689 COP | Water Cooled Chiller, 4.689 COP | Water Cooled Chiller, 4.689 COP | Water Cooled Chiller, 5.172 COP
Chiller Pump Control, Pump Power | NA | Constant Primary (4 W/GPM), Variable Secondary (12 W/GPM) | Constant Primary (3.2 W/GPM), Variable Secondary (10.8 W/GPM) | Constant Primary (4 W/GPM), Variable Secondary (12 W/GPM) | Constant Primary (3.2 W/GPM), Variable Secondary (10.8 W/GPM) | Constant Primary (4 W/GPM), Variable Secondary (12 W/GPM) | Constant Primary (3.2 W/GPM), Variable Secondary (10.8 W/GPM)
Cooling Tower Efficiency |  | NA | NA | 38.2 | 40.2 | 38.2 | 40.2
Fan Control, Fan Power (W/CFM) | On-Off, 0.528 W/CFM | On-Off, 0.16 W/CFM | On-Off, 0.16 W/CFM | VAV, 1.135 W/CFM | VAV, 1.021 W/CFM | VAV, 1.135 W/CFM | VAV, 0.9825 W/CFM
Reheat Source | NA | NA | NA | HW Reheat | HW Reheat | Electric Reheat | Electric Reheat
Minimum Airflow Fraction | NA | NA | NA | 0.3 | 0.2 | 0.3 | 0.2
Economizer Control | NA | Yes | Yes | Yes (100% Eff) | Yes (100% Eff) | Yes (100% Eff) | Yes (100% Eff)
ERV (Y/N) | NA | NA | NA | No | Yes | No | Yes
ERV Sensible, Latent Effectiveness | NA | NA | NA | NA | 0.70, 0.60 | NA | 0.70, 0.60
DCV Control | No | No | No | No | Yes (50% of Area) | No | Yes (50% of Area)
WLHP Cooling Tower Efficiency | 38.2 | NA | NA | NA | NA | NA | NA
WLHP Boiler Efficiency | 80% Et | NA | NA | NA | NA | NA | NA
DOAS Details |  |  |  |  |  |  | 
Coupled with DOAS System? | Yes | Yes | Yes | No | No | No | No
DOAS Cooling Source, Efficiency | No Cooling | DX, 3.461 COP | DX, 3.461 COP | NA | NA | NA | NA
DOAS Heating Source, Efficiency | No Heating | Gas Furnace, 80% Et | Gas Furnace, 93% Et | NA | NA | NA | NA
DOAS Fan Control, Fan Power | VAV, 0.778 W/CFM | VAV, 0.258 W/CFM | VAV, 0.258 W/CFM | NA | NA | NA | NA
ERV (Y/N) | Yes | Yes | Yes | NA | NA | NA | NA
ERV Sensible, Latent Effectiveness | 0.7, 0.0 | 0.5, 0.5 | 0.70, 0.65 | NA | NA | NA | NA